## Site_Estab_01
Provisional Bill of Quantities - Construction of Electrical Infrastructure - Onayena Street Lights 2023
| Description | Unit | Qty | Labour Rate | Material Rate | Total Rate | Total (Qty*Total)
1 | PRELIMINARY AND GENERAL | [5 empty] | * * * * * * * * * * * * * * *
| General P and G's | [5 empty] | * * * * * * * * * * * * * * *
1.1 | Establishment of Site | Item | 1 | - | -
1.2 | Setting out of works | Item | 1 | - | -
1.3 | Insurances as per Procurement Contract | Item | 1 | - | -
1.4 | Performance Guarantee as per Procurement contract | Item | 1 | - | -
1.5 | Commissioning of the complete installation as specified and requested by the Engineer | Item | 1 | - | -
1.6 | Transport of Project Materials to site | Item | 1 | - | -
| Others - Please specify | [5 empty] | * * * * * * * * * * * * * * *
1.7 |  | Item | 1
| Carried forward to BID SUMMARY |  |  |  |  | TOTAL | 0

## Streetlighting-2.1
Provisional Bill of Quantities - Construction of Electrical Infrastructure - Onayena Street Lights 2023
| Description | Unit | Qty | Labour Rate | Material Rate | Total Rate | Total (Qty*Total)
n/a
5 | STREET- LIGHTING : (Luminaires, Control gear, Steel Poles and Accessories) | [5 empty] | * * * * * * * * * * * * * * *
5.1 | U/G Cables feeding from different distribution boards to lighting poles- PVC SWA PVC 600/1000V UNDERGROUND Cu Cable system. (Length to be measured along straight lines- provision for the cable lengths to poles (T-OFFS) should also be measured.) Rate includes for installation of cable (labour rate) | [5 empty] | * * * * * * * * * * * * * * *
a | 4 x 16 mm² Cu underground cable for street lighting | m | 0 |  |  |  | Rate Only
b | 4 x 10 mm² Cu underground cable for street lighting | m | 0 |  |  |  | Rate Only
c | 4 x 6 mm² Cu underground cable for street lighting | m | 280
g | Earth-wire - SABS - 10 mm² BCEW | m | 0 |  |  |  | Rate Only
h | Earth-wire - SABS - 6 mm² BCEW | m | 280
5.2 | Termination and Joints of PVC SWA Cu Cable. Terminations in DB/Control-board with CCG glands to specification and Inline-joints (Scotchcast) to specs | [5 empty] | * * * * * * * * * * * * * * *
a | terminate complete in DB on CCG gland - up to 4x16 mm² Cu cable and BCEW as above | No | 1
b | T-joint for up to 4x10 mm² Cu cable as above (Scotchcast 3M 91T2) | No | 0 |  |  |  | Rate Only
c | In-line cable joints for up to 4x10 mm² Cu cable as above (Scotchcast 3M ) | No | 0 |  |  |  | Rate Only
5.3 | Cable sleeves and cable markers | [5 empty] | * * * * * * * * * * * * * * *
a | Sleeves - 110mm diameter, PVC class 6 in 6m lengths | No | 0 |  |  |  | Rate Only
b | Roadcrossing under culvert - 50mm galvanised steel pipe - protection around cables to be fed under existing culverts | item | 0 |  |  |  | Rate Only
c | Cable markers - concrete 10MPa (300x300 bottom, 150x150mm top, 500mm high), with descriptive plate, as specified | No | 0 |  |  |  | Rate Only
5.4 | Trenching for feeder cables. (from streetlighting control boards to streetlight poles and as required and between lightpoles) . | [5 empty] | * * * * * * * * * * * * * * *
a | Trenching - 700 mm deep, 400 mm wide, in ground (handtools) - to SABS - incl. Backfilling, and laying of danger tape. | m | 270
b | Trenching - 700 mm deep, 400 mm wide, in soft rock (jack-hammer excavation, - to SABS - incl. Backfilling with sand, and laying of danger tape. | m | 0 |  |  |  | Rate Only
| Carried forward to NEXT PAGE |  |  |  |  | TOTAL | 0

## Streetlighting+Ctrl-2.2
Provisional Bill of Quantities - Construction of Electrical Infrastructure - Onayena Street Lights 2023
| Description | Unit | Qty | Labour Rate | Material Rate | Total Rate | Total (Qty*Total)
| Brought forward from previous sheet: | [5 empty] | 0
5 Con. | STREET- LIGHTING : (Luminaires, control gear, steel poles and Accessories) | [5 empty] | * * * * * * * * * * * * * * *
5.5 | STREET-LIGHTING LUMINAIRES - completely supplied and delivered - as specified - side / bottom entry. The luminaire shall consist of a separate lamp, gear and spigot compartment. It is shall be designed to operate LED Segments lamps. The luminaire shall bear the SABS 1277 mark and the SABS 1464 safety mark. Luminaire spigot entries shall comply with SABS 1088 - Table 1.Side entry - 42mm ø x 125mmBottom entry - 76mm ø x 75mmThe luminaire shall have a degree of protection that complies with SABS 1222 and SABS 098: Part 1 - 1990 Code of Practice Table B-1:Lamp compartment: IP66Gear compartment: IP66The IP ratings shall be certified by SABS test reports. | [5 empty] | * * * * * * * * * * * * * * *
5.5.1 | Streetlighting luminaire EQUAL to BekaLEDLume-XP2 40LED/88W, neutral white light (4000K), Optic 5305, SE (Side Entry) as specified installed. Specify type: | No | 7
5.5.2 | Connection cable from bottom access inspection hole to luminaire, complete installed and connected to each individual luminaire, allow for 3x4mm² Cu cable. (Terminal strip and terminals/termination glands are measured as part of the poles structure) | No | 7
5.6 | LIGHTPOLES | [5 empty] | * * * * * * * * * * * * * * *
The pole shall be continuously tapered and of circular cross-section. Design and construction to SABS 0255-1991. All tubing to SABS 657 – grade 250 Mpa. Unlimited tensile strength 450 Mpa. Fabrication of poles to SABS 0214-1987 . Design fabrication and inspection on articles for: Hot dip galvanizing to SABS 763. The pole shall sustain , in addition to other loads , a maximum wind loading of 3 seconds gust wind at not less than 120 km/h on the exposed surface of the complete lighting installation. The maximum permissible deflection at the top of the poles shall not exceed one fortieth (1/40) of the height of the pole . The weight of the lantern that will be mounted is 20 kg with a vertical projected area of 0.33 m ² The size and length of open –ended spigot required on the end shall be 76mm O.D. x 100 mm . The equipment mounting plate incorporated with the gland plate should be provided with ONE 6 A, 2.5kA Shrouded MCB and 5 x UK 25N terminals with 2x E-UK stoppers all mounted on a Din Rail . As required, UK50N terminal blocks shall be used to connect junction points with more than three infeed points, and the terminal rail can then be mounted vertically. The gland plate should be drilled with 4 only x 25 mm² holes etc. - Up to three size 2 Prately cable glands, nikel plated, completely terminating the cables, shall be included in the rate. The top of the terminals shall be covered with a gms plate overhag to prevent condensate water to drip on the terminal rails. Each pole shall have two cables entries (Opposite) 450 mm below ground level .The slot Shall measure 100x 50 mm . The door shall be fitted with a waterproof cover plate to be secured by a recessed seven Side nut . Ventilation apertures shall be provided in the cover plate and shall be vermin and weatherproof. All sections , parts etc. shall be hot – dipped galvanized after manufacture to SABS 763 Specification and shall be of pleasing aesthetic appearance. The planting depth , plus 450mm of the pole , shall be painted with two coats of durable Epoxy tar paint after galvanizing . Plus glassfibre sleeve. The tenderer shall submit with his tender detailed engineering drawings together with a Copy of the relevant test certificate and shall give proof of the safety factor applied. The pole shall be delivered complete with base plate ,access door cover, fixing screws and hook bolts.
5.6.1 | Supply, deliver, install, align - Galvanised steel streetlighting Pole - including equipment mounting plate, Circuit breaker, cable glands, terminations - complete wired. Mounting Height : 8,00m (– 9.2m) - or as specified Planting depth (not less than): 1,20M Access door to control gear: 300mm x127mm Height of access door above Ground level 700 - 800mm Base plates (not less than) 400mm x 400 mm x 4mm 76mm top diameter, 3.5x6000mm / 127 bottom diameter, 3.5x3200mm) (Refer to detail as specified above). | [5 empty] | * * * * * * * * * * * * * * *
or equal - alternatives can be offered
a | 9.2m Pole as specified above, completely planted 1.2m deep, pole top 8 m above ground-level with 400x400x4 mm baseplate. | No | 7
5.6.2 | Pole Top mounting Adaptor | [5 empty] | * * * * * * * * * * * * * * *
a | SINGLE SIDE MOUNTING ADAPTOR, HDG, - 15° Degree upward inclination, 150mm long and 42mm OD outreach, adaptor to be fitted over the pole - open ended spigot adaptor shall be 76mm OD, 100mm high | No | 7
| Carried forward to BID SUMMARY |  |  |  |  | SUB - TOTAL | 0

## Cont_04
Provisional Bill of Quantities - Construction of Electrical Infrastructure - Onayena Street Lights 2023
| Description | Unit | Qty | Labour Rate | Material Rate | Total Rate | Total (Qty*Total)
3 | GENERAL ITEMS, PC ITEMS AND CONTINGENCIES | [5 empty] | * * * * * * * * * * * * * * *
3.1 | Contingency - | Item | 1 | ---------------- |  | 15000 | 15000
3.2 | NORED Admin Fees | Item | 1 |  |  | 5000 | 5000
| Carried forward to BID SUMMARY |  |  |  |  | SUB - TOTAL | 0

## Summary
Provisional Bill of Quantities - Construction of Electrical Infrastructure - Onayena Street Lights 2023
I. | DESCRIPTION
1 | PRELIMINARY AND GENERAL | 0
2 | STREET- LIGHTING : (Luminaires, Control gear, Steel Poles and Accessories) | 0
3 | GENERAL ITEMS, PC ITEMS AND CONTINGENCIES | 0
II. | Sub Total EXCL. VAT | 0
III. | 15% VAT (on item II.) | 0
IV. | TOTAL PROJECT WORKS incl. 15% VAT (item II. + III.) | 0